## Summary
Organization | Qatar Red Crecent
Activity | BOQ of Construction activities and Water Distributions Networks
Village | Holhol or Fallaydhyale
District | Lascanood
Summary
NO. | Description | Qty | Rate | Amount USD
1 | Borehole Drilling (200 to 250 m) and Installation | 1
2 | Elevated Water Tank 30 m3 | 1
3 | Generator Room | 1
4 | Caretaker Room | 1
5 | Communal Water Point | 1
6 | Animal Water Troughs | 2
7 | Fence and Gate | 1
Total

## Borehole Drilling
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | TOTAL (USD)
1. PROPOSED BOREHOLE DRILLING
Baidoa District
A | Hydrogeophysical Survey | 1 | LS
B | BOREHOLE DRILLING AND INSTALLATION
1 | SITE WORKS
1.1 | Allow for the cost of mobilization of all equipment, consumables for the entire borehole works and drilling team to the site and demobilization from the site | 1 | Item
1.2 | Site clearance, levelling and other associated costs | 1 | Item
1.3 | Setting up and dismantling of the rig at the drilling site | 1 | Item
1.4 | Other related tasks such as water for drilling and camp use, maintenace of storage tanks, water injection systems and usage of drilling foam | 1 | Item
| Total carried forward to summary page |  |  |  | 0
2 | BOREHOLE DRILLING
Drilling to a minimum of 12" and to an acceptable minimum depth as per hydro geological report:
2.1 | Drilling with min. 17" bit from 0-10m depth | 10 | m
2.2 | Drilling with min. 12" bit from 10m-240m depth | 240 | m
2.5 | Soil sampling and record keeping as detailed in specification | 1 | Item
| Total carried forward to summary page |  |  |  | 0
3 | BOREHOLE INSTALLATION
Installation of PVC casings were applicable except for areas where screen casings will be installed
3.1 | Supply and installation of surface casing 14" (external Diameter). Minimum thickness 3mm. Upto 10m depth | 10 | m
3.2 | Supply and installation of PVC casing ( plain or slotted) 8.625" minimum diameter. Minumum thickness 3mm up to 200m depth | 250 | m
3.3 | Supply and install gravel pack in the borehole as detailed in the specification | 7 | Ton
Total carried forward to summary page
4 | BOREHOLE DEVELOPMENT
4.1 | Allow for borehole development work (surging by air of the completed well until the water is clean (Approx. 3hrs) | 3 | Hr
4.2 | Pump testing for the well of the well using a submersible pump for at least 24- 36 hours to estimate draw down and the yield | 24 | Hr
4.3 | Provide all materials and construct concrete top slab with well cap and engraving serial number | 1 | Sum
4.4 | Standby charges for reasons beyond contractor's control excluding force majeure conditions | 1 | Hr
4.5 | Borehole Completion Report and Water Chemical Analysis Report | 1 | Sum
| Total carried forward to summary page |  |  |  | 0
5 | Pump Installation with Generator Set
5.1 | Supply and installation of new 15 Hp Lowara submersible pump | 1 | Item
5.2 | Supply and installation of rising main GI pipe 2” with all necessary fittings | 35 | Item
5.3 | Supply and Installation of New Generator Set, KVA: 30 Engine Type: Perkins 1103A-33G, Open / Volts: 400 / 230 v, Cycles Hz: 50 Volts, R.P.M: 1500 ¦ Fuel Consumption: 8.3 Litre/hr, diesel driven, 3 phase water cooled | 1 | Item
5.4 | Cables of 150 meter per BH and fittings | 250 | M
5.5 | Controal Panel | 1 | Item
5.6 | Water meter | 1 | Item
Supply and Installation of Solar powered pump comprising of 40 No. Modules of 325 wp Poly crystalline
5.8 | Grundfos RSI Inverter 3x380V IP66 15kW 31A | 1 | Item
5.9 | SOLAR PANELS 325Wp Poly crystalline | 40 | Item
5.1 | PV Disconnect 1000-40-5 | 1 | Item
5.11 | 16mm2 submersible pump 3-phase drop cable | 250 | m
5.12 | Well Probe Cable | 250 | m
5.13 | Well probe sensor | 1 | Item
5.14 | Cable splice kit 6-10sqmm | 2 | Item
5.15 | Float switch | 1 | Item
5.16 | Surge Protector | 1 | Item
5.17 | Change over switch 100 Amps | 1 | Item
5.18 | Mounting structure | 40 | Item
Total carried forward to summary page
Summary Page
1 | Hydrogeophysical Survey |  |  |  | 0
1 | Site works |  |  |  | 0
2 | Borehole drilling |  |  |  | 0
3 | Borehole installation
4 | Borehole development |  |  |  | 0
5 | Pump Installation
| Total carried forward to Grand Summary page |  |  |  | 0

## Elevated water tank
ITEM | DESCRIPTION |  | UNIT | QNTY | RATE US$ | AMT US$
2. ELEVATED WATER TANK 30 M3
Baidoa DISTRICT
ELEMENT NO. 1 : SITE PREPARATION
A | Clear site of all bushes and debris. Grab up roots and |  | m2 | 12
burn the arisings
B | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  | Item | 1
| Total carried to summary |  | $
ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
A | Top soil excavation average 200mm deep |  | m3 | 2.4
B | Excavate for foundation not exceeding 0.3
| meters deep, starting from stripped levels |  | m3 | 0.24
| Extra over for excavation in rock |  | m3 | 3
Ditto
| Column bases |  | m3 | 30
Planking and strutting
C | Allow for keeping foundations free from water, mud, fallen
| materials, etc. |  | LS | 1
Disposal
D | Return, fill and ram selected excavated material around
| foundations |  | m3 | 9
E | Load, wheel and cart deposit and spread surplus
excavated material where directed on site at a
| distance not exceeding 100 meters |  | m3 | 21
Hardcore or other approved filling, as described
F | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed |  | m2 | 0.72
G | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled |  | m2 | 20
smooth to receive polytheen sheeting (m.s)
Anti-termite treatment
H | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of blinding |  | m2 | 20
Damp-proof membrane
I | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) |  | m2 | 20
| Total carried to summary |  | $ |  |  | #VALUE!
ELEMENT NO. 3 : CONCRETE WORKS
Plain concrete class 15 in:
A | 100mm blinding |  | m3 | 2
| Ditto for column bases |  | m3 | 0.864
Insitu concrete class 25/20 , vibrated and reinforced with 60mm thick
maximum aggregate size in as described, in:-
BEAMS
A | Ground beam |  | m3 | 0.99
B | Ring beam 1 |  | m3 | 0.99
C | Ring beam 2 |  | m3 | 1.98
COLUMNS
A | Columns bases |  | m3 | 4.32
B | Starter columns |  | m3 | 0.96
C | Columns (Height 6m) |  | m3 | 5.76
SLABS
A | 200mm thick surface bed laid in bays including all
| necessary formwork |  | m3 | 2.4
Ditto:
B | Suspended slab |  | m3 | 2.4
C | 150mm thick Roof slab |  | m3 | 3
Walls
E | 150mm thick RC wall |  | m3 | 5.03
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461 including
cutting bending and tying
BEAMS
GROUND BEAM
A | Y12 (Nominal Diameter 12mm) bars as main bars,
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 97.68
B | R8 (Nominal Diameter 8mm) bars as rings,
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) |  | Kg | 38.236
RING BEAM 1
C | Ditto for Y12 as main bars |  | Kg | 97.68
D | Ditto for R8 as rings |  | Kg | 38.236
RING BEAM 2
C | Ditto for Y12 as main bars |  | Kg | 214.896
D | Ditto for R8 as rings |  | Kg | 38.236
COLUMNS
COLUMN BASES
A | Y14 (Nominal Diameter 14mm) bars as main bars,
| Cross-Sectional Area (154mm2), Mass per unit length (1.209kg/m) |  | Kg | 174.096
STARTER COLUMNS
B | Y16 (Nominal Diameter 16mm) bars as main bars,
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) |  | Kg | 113.688
C | R8 (Nominal Diameter 8mm) bars as rings,
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) |  | Kg | 14.22
COLUMNS
6m HIGH COLUMNS
D | Y16 (Nominal Diameter 16mm) bars as main bars,
| Cross-Sectional Area (201mm2), Mass per unit length (1.579kg/m) |  | Kg | 454.752
E | R8 (Nominal Diameter 8mm) bars as rings,
| Cross-Sectional Area (50.3mm2), Mass per unit length (0.395kg/m) |  | Kg | 85.32
SLABS
ROOF SLAB
A | Y12 (Nominal Diameter 12mm) bars as main bars tops 1
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 56.83
B | Y12 (Nominal Diameter 12mm) bars as main bars tops 2
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 53.28
C | Y12 (Nominal Diameter 12mm) bars as main bars bottom 1
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 56.83
D | Y12 (Nominal Diameter 12mm) bars as main bars bottom 2
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 53.28
BASE SLAB
A | Y12 (Nominal Diameter 12mm) bars as main bars tops 1
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 56.83
B | Y12 (Nominal Diameter 12mm) bars as main bars tops 2
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 53.28
C | Y12 (Nominal Diameter 12mm) bars as main bars bottom 1
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 56.83
D | Y12 (Nominal Diameter 12mm) bars as main bars bottom 2
| Cross-Sectional Area (113mm2), Mass per unit length (0.888kg/m) |  | Kg | 53.28
WALLS
A | Y10 (Nominal Diameter 12mm) bars as main bars tops 1
| Cross-Sectional Area (79mm2), Mass per unit length 0.617kg/m) |  | Kg | 213.2352
B | Y10 (Nominal Diameter 12mm) bars as main bars tops 1
| Cross-Sectional Area (79mm2), Mass per unit length 0.617kg/m) |  | Kg | 213.2352
Reference A142 mesh 200 x 200 mm , weight 2.22 kgs per
square meter ( measured net - no allowance made for laps
(inclunding bends, tying wire and distance blocks)
A | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed |  | m2 | 20
Sawn formwork as described to:-
B | To edge of floor slab |  | m2 | 3.6
C | Ditto to sides and soffits of roof slab |  | m2 | 2.7
D | Ditto to sides and soffits of base slab |  | m2 | 3.6
E | Ditto to walls |  | m2 | 50.4
| Total carried to summary |  | $ |  |  | #VALUE!
ELEMENT NO. 4 : Finishing
Plastering
Insitu concrete class 25/20 , vibrated and reinforced with 60mm thick
maximum aggregate size in as described, in:-
A | 200 mm thick reinforced wall |  | m3 | 10.08 |  | 0
| Total carried to summary |  | $ |  |  | 0
0
2. ELEVATED WATER TANK 30 M3
0
ELEMENT NO. 6 : FINISHES
Cement and sand (1:3) screeds, backings, beds etc
A | 25mm Thick cement/sand (1:4) screed finish
| Floor slab |  | m2 | 20 |  | 0
B | 15 mm cement and sand (1:3) render, finished with
wood float to:-
Concrete or masonry surfaces externally
| Outside roof slab |  | m2 | 20 |  | 0
| Ditto outside base slab |  | m2 | 20 |  | 0
| Ditto Outside walls |  | m2 | 54 |  | 0
| Ditto for columns |  | m2 | 86.4 |  | 0
C | Lightweight water proofed screeds and plaster
15 mm cement and sand (1:3) render, finished with
steel float to:-
Concrete or masonry surfaces internally
| Inside roof top slab |  | m2 | 20 |  | 0
| Ditto inside base slab |  | m2 | 20 |  | 0
| Ditto inside walls |  | m2 | 54 |  | 0
Painting
D | Fill uneven surfaces with stucco filler to approval and apply
two coats soft white external textured paint to:
| Plastered and rendered surfaces |  | m2 | 180.4 |  | 0
E | Prepare surfaces and apply three coats gloss oil paint as 'Crown'
or equal and approved manufacturer(s) on concrete and masonry
surfaces: measured overall on both sides
| Plastered surfaces internally and externally |  | m2 | 180.4 |  | 0
| Total carried to summary |  | $ |  |  | 0
0
2. ELEVATED WATER TANK 30 M3
0
ELEMENT NO. 7 : PLUMBING INSTALLATIONS
A | Galvanized Mild Steel pipes class "B" medium thickness with and
including jointing, fittings and fixe as described
| Supply and install 50mm diameter inlet pipe 800mm long |  | No. | 1 |  | 0
| Supply and install 50mm diameter draw off pipe Ditto |  | No. | 1 |  | 0
| Supply and install 50mm diameter overflow pipe Ditto |  | No. | 1 |  | 0
| Supply and install 75mm diameter scour pipe Ditto |  | No. | 1 |  | 0
| Supply and install 20mm diameter brass gate valve with wheel and head |  | No. | 1 |  | 0
| Supply and install 20mm diameter stop corks |  | No. | 1 |  | 0
Cement and sand mortar (1:3) rendering in:
A | 25 mm Thick screed to base slab with waterproof cement |  | m2 | 2.8
B | 15mm internal plaster to cover slab with waterproof cement |  | m2 | 9.99
C | 15mm plaster to internal sides of wall with waterproof cement |  | m2 | 22.2
D | 12mm plaster to external sides of wall |  | m2 | 21
E | 12mm plaster to cover slab |  | m2 | 12
F | 12mm plaster to Ground beams |  | m2 | 13.76
G | 12mm plaster to Ring 1 beams |  | m2 | 20.64
H | 12mm plaster to Ring 2 beams |  | m2 | 20.64
I | 12mm plaster to columns |  | m2 | 57.6
| Total carried to summary |  | $
Element No 5: Plumbing installation
Galvanized Mild Steel pipes class "B" medium thickness
with and including jointing, fittings and fixe as described
A | Supply and install 50mm diameter inlet pipe 800mm long |  | NO | 1
B | Supply and install 50mm diameter draw off pipe Ditto |  | NO | 1
C | Supply and install 50mm diameter overflow pipe Ditto |  | NO | 1
D | Supply and install 75mm diameter scour pipe Ditto |  | NO | 3
E | Supply and install 20mm diameter brass gate valve with wheel and head |  | NO | 1
F | Supply and install 20mm diameter stop corks |  | NO | 3
G | 600x600x6mm heavy gauge steel primed metal manhole
| cover on slab with and including metal framing all around |  | NO | 1
| Total carried to summary |  | $
MAIN SUMMARY
| Ref. | ELEMENT |  | PAGE |  | AMOUNT
| 1 | ELEMENT NO. 1 : SITE PREPARATION |  | 5/1
| 2 | ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL) |  | 5/2
| 3 | ELEMENT NO. 3 : CONCRETE WORKS |  | 5/3
| 4 | ELEMENT NO. 4 : Finishing |  | 5/6
| 8 | Element No 5: Plumbing installation |  | 5/8
TOTAL CARRIED TO GRAND SUMMARY |  |  | US$ |  |  | 0

## Generator Room
ITEM NO. | DESCRIPTION |  | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
3. GENERATOR ROOM
ELEMENT NO. 1
SITE PREPARATION
A | Clear site of all trees, bushes and shrubs, grab up roots and
| burn the arisings. |  | m2 | 22
B | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  | LS | 1
| CARRIED TO COLLECTION AT END OF ELEMENT 1 |  | US$
ELEMENT NO. 2
SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
A | Excavate trench for foundation not exceeding 1.50 meters
| deep, starting from stripped levels |  | CM | 3.3
Disposal
B | Return, fill and ram selected excavated material around
| foundations |  | CM | 2.2
Hardcore or other approved filling, as described
D | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed |  | SM | 22
Anti-termite treatment
E | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of hard-core |  | SM | 22
Damp-proof membrane
F | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) |  | SM | 22
Plain concrete class 15 in:
G | 50mm blinding under strip footing |  | SM | 2
Reinforced concrete class (20) as described, in:-
H | Strip footing |  | CM | 1.6
I | 125mm thick surface bed laid in bays including all
| necessary formwork |  | CM | 2.5
J | Ditto for generator plinths |  | CM | 0.675
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461
FOOTING
A | 10mm bars |  | Kg | 37.02
B | 8mm bars |  | Kg | 22.12
Mesh fabric reinforcement to B.S 4483 and setting in
concrete with 300mm side and end laps
(measured nett-allow for laps).
C | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed |  | SM | 26
D | Ditto for generator plinth |  | SM | 4.8
E | Ditto for ramp |  | SM | 7
Sawn formwork as described to:-
F | To edge of steps and slabs over 75mm but not exceeding
| 150mm high |  | LM | 24
G | Sides and soffits of lintols |  | LM | 2
H | Sides and generator plinth |  | LM | 12.8
| CARRIED TO COLLECTION AT END OF ELEMENT 2 |  | US$
ELEMENT NO. 3
WALLING
SUBSTRUCTURE WALLING
Approved compacted rubble stone fill bedded and jointed in
cement sand mortar (1:4)
A | 400mm thick rubble stone foundation walling |  | m3 | 6.4
SUPERSTRUCTURE WALLING
200x400mm hollow block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
B | 200mm thick walling Super-structure walling |  | SM | 27
C | Ditto for dwarf wall |  | SM | 10.4
Damp-proof courses, as described, to walls
D | 200mm wide |  | LM | 37.4
E | 100mm dia. Galvanized Circular Hollow Section (CHS)poles |  | No. | 4
F | Heavy duty fabric mesh |  | SM | 26
G | 150x50mm timber framework |  | LM | 24
| CARRIED TO COLLECTION AT END OF ELEMENT 3 |  | US$
ELEMENT NO. 4
ROOF CONSTRUCTION AND FINISHES
The following in sawn cellcured timber roof trusses with nailed
connections including hoisting and fixing in position
not exceeding 5.0 meters above ground floor level
A | 100x50mm rafters |  | LM | 60
B | 100x50mm strut or tie |  | LM | 30
C | 100x50mm tie beam |  | LM | 35
D | 100x50mm wall plate fixed with and including 200mm
long 12mm diameter rag bolts cast into beam at 1500mm
| centres |  | LM | 20
E | 200mm x 25mm Fascia Board |  | LM | 22
Roof sheets as IT4 profile gauge 28 pre-painted galvanised
F | Roof sheets as IT4 profile gauge 28 pre-painted galvanised
roofing sheets laid with 95 mm side and 200 mm end laps
| hook bolts, PVC washer and tropicalized slip cup |  | SM | 38
| CARRIED TO COLLECTION AT END OF ELEMENT 4 |  | US$ |  |  | #VALUE!
ELEMENT NO. 5
FINISHES
15 mm cement and sand (1:3) render, finished with
woodfloat to:-
A | Concrete or masonry surfaces internally and externally |  | SM | 37.4
12mm (minimum) two coat lime plaster as described to
B | Concrete or masonry surfaces internally |  | SM | 37.4
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
C | 40mm bed finished floor screed |  | SM | 32
Painting and decorating
Prepare and apply three coats first quality emulsion
paint on:-
D | Plastered walls externally |  | SM | 37.4
Prepare and apply three coats first quality silk vinyl
emulsion paint on:-
E | Plastered surfaces internally |  | SM | 37.4
| CARRIED TO COLLECTION AT END OF ELEMENT 5 |  | US$
ELEMENT NO. 6
DOORS
Purpose built steel door complete with heavy gauge
mesh on 2" diameter galvanized iron framework.
framework including cutting handling, hoisting fixing in position
at all heights with all necessary ironmongery and
applying a priming coat of approved steel primer.
A | Double door overall size 2800x2100mm high |  | No. | 1
double leaf
B | Single door overall size 900x2100mm high
| single leaf |  | No. | 1
Allow for PCC vents which are meshed wire
C | windows 1500X1500mm high |  | LS | 3
| CARRIED TO COLLECTION AT END OF ELEMENT 6 |  | US$ |  |  | #VALUE!
ELEMENT NO. 7
ELECTRICAL INSTALLATION AND SERVICES
Lighting Fittings
Supply and install following lighting fixtures with all accessories
as per the specifications and drawings and complete with lamp
fitting and accessories of Engineer or approved make.
A | 1200mm flourescent tube lighting |  | No. | 3
| 150W LED floodlight |  | No. | 1
Switches
B | 5 Amps 3 gang one way switch |  | No | 1
C | 5 Amps 2 gang one way switch |  | No | 1
Socket outlets
Supply and installation of fused shuttered switched socket outlet
to comply with relevant BS standard (Clipsal, Orange, Crabtree/
Tenby/ABB or equivalent). Wiring (including supply of earth wire
and all other material required) of above socket outlet using approved
type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn
through securely fixed concealed PVC conduit in a ring circuit.
Socket outlet points
D | 13 A twin sockets outlet |  | No | 2
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with
all required accessories for proper installation and operation including
conduits, pipes( each cable in separate conduit or pipe), cable lugs,
ties... etc. as shown on drawing, as per the preamble, the specifications
and supervision engineer's requirements.
E | Supply, install and connect complete 1.5 sq. mm colour-coded SC
cables to lighting points drawn in Concealed /surface 20mm HG PVC
conduits, complete with draw boxes, switch boxes and other necessary
| accessories. |  | M | 10
F | Supply and install two compartment floor recessed metallic electrical
floor box with flap cover complete with lifting handle, cable cable flaps,
| as Crabtree Britmac or equal and approved |  | No. | 1
| CARRIED TO COLLECTION AT END OF ELEMENT 7 |  | US$ |  |  | #VALUE!
MAIN SUMMARY
| ELEMENT | TITLE |  | PAGE |  | AMOUNT
NO
| 1 | SITE PREPARATION |  | 2/1
| 2 | SUBSTRUCTURES (PROVISIONAL) |  | 2/2
| 3 | WALLING |  | 2/3
| 4 | ROOF CONSTRUCTION AND FINISHES |  | 2/4
| 5 | FINISHES |  | 2/5
| 6 | DOORS |  | 2/6
| 7 | ELECTRICAL INSTALLATION AND SERVICES |  | 2/7
TOTAL CARRIED TO GRAND SUMMARY |  |  | US$ |  |  | #VALUE!

## Caretakers room
ITEM NO. | DESCRIPTION |  | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
4. CARETAKERS ROOM
ELEMENT NO. 1: SITE PREPARATION
A | Clear site of all trees, bushes and shrubs, grab up roots and
| burn the arisings. |  | SM | 14.52
B | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  | LS | 1
| CARRIED TO COLLECTION AT END OF ELEMENT 1 |  | US$ |  |  | #VALUE!
ELEMENT NO. 2: SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
A | Topsoil excavation average 200mm deep |  | CM | 3.08
B | Excavate trench for foundation not exceeding 1.50 meters
| deep, starting from stripped levels |  | CM | 9.24
Disposal
C | Return, fill and ram selected excavated material around
| foundations |  | CM | 6.16
D | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  | CM | 3.08
Hardcore or other approved filling, as described
E | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed |  | CM | 4.74
Anti-termite treatment
F | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of hard-core |  | SM | 4.74
Damp-proof membrane
G | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) |  | SM | 4.74
Plain concrete class 15 in:
H | 50mm blinding under strip footing |  | SM | 8.7
Reinforced concrete class (20) as described, in:-
I | Ground beam |  | CM | 1.848
J | Litols |  | CM | 1.08
K | 200mm thick surface bed laid in bays including all
| necessary formwork |  | CM | 2.9
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461
A | GROUND BEAM
| 10mm bars |  | Kg | 152.0288
| 8mm bars |  | Kg | 17.0324
B | LINTOLS
| 10mm bars |  | Kg | 2.9616
| 8mm bars |  | Kg | 1.3272
Mesh fabric reinforcement to B.S 4483 and setting in
concrete with 300mm side and end laps
(measured nett-allow for laps).
C | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed |  | SM | 4.74
Sawn formwork as described to:-
D | To edge of slab |  | SM | 3.08
E | To edge of steps and slabs over 75mm but not exceeding
| 150mm high |  | SM | 0.4
F | Sides and soffits of lintols |  | SM | 0.6
| CARRIED TO COLLECTION AT END OF ELEMENT 2 |  | US$
ELEMENT NO. 3: WALLING
SUBSTRUCTURE WALLING
Approved compacted rubble stone fill bedded and jointed in
cement sand mortar (1:4)
A | 400mm thick rubble stone foundation walling |  | m3 | 4.928
SUPERSTRUCTURE WALLING
200x400mm hollow block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
B | 200mm thick walling Super-structure walling |  | SM | 41.58
Damp-proof courses, as described, to walls
C | 200mm wide |  | LM | 15.4
| CARRIED TO COLLECTION AT END OF ELEMENT 3 |  | US$ |  |  | #VALUE!
ELEMENT NO. 4: ROOF CONSTRUCTION AND FINISHES
The following in sawn cellcured timber roof trusses with nailed
connections including hoisting and fixing in position
not exceeding 5.0 meters above ground floor level
A | 100x50mm rafters |  | LM | 20
B | 100x50mm collar |  | LM | 6
C | 100x50mm tie beam |  | LM | 16
D | 100x50mm wall plate fixed with and including 200mm
long 12mm diameter rag bolts cast into beam at 1500mm
| centres |  | LM | 15.4
Roof sheets as IT4 profile gauge 28 pre-painted galvanised
E | Roof sheets as IT4 profile gauge 28 pre-painted galvanised
roofing sheets laid with 95 mm side and 200 mm end laps
| hook bolts, PVC washer and tropicalized slip cup |  | SM | 26
F | 25mm soft board ceiling |  | SM | 14.5
| CARRIED TO COLLECTION AT END OF ELEMENT 4 |  | US$ |  |  | #VALUE!
ELEMENT NO. 5: FINISHES
15 mm cement and sand (1:3) render, finished with
woodfloat to:-
A | Concrete or masonry surfaces internally and externally |  | SM | 41.58
12mm (minimum) two coat lime plaster as described to
B | Concrete or masonry surfaces internally |  | SM | 41.58
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
C | 40mm bed finished floor screed |  | SM | 4.74
Painting and decorating
Prepare and apply three coats first quality emulsion
paint on:-
D | Plastered walls externally |  | SM | 41.58
Prepare and apply three coats first quality silk vinyl
emulsion paint on:-
E | Plastered surfaces internally |  | SM | 41.58
F | Soffits of ceiling |  | SM | 14.5
| CARRIED TO COLLECTION AT END OF ELEMENT 5 |  | US$ |  |  | #VALUE!
ELEMENT NO. 6: DOORS
Purpose built steel door complete with heavy gauge
mesh on 2" diameter galvanized iron framework.
framework including cutting handling, hoisting fixing in position
at all heights with all necessary ironmongery and
applying a priming coat of approved steel primer.
A | Single door overall size 900x2100mm high
| single leaf |  | No. | 1
Allow for PCC vents
B | 1000X300mm high |  | LS | 3
C | Window overall size 1000x1000mm high |  | No | 2
| CARRIED TO COLLECTION AT END OF ELEMENT 6 |  | US$ |  |  | #VALUE!
ELEMENT NO. 7: ELECTRICAL INSTALLATION AND SERVICES
Lighting Fittings
Supply and install following lighting fixtures with all accessories
as per the specifications and drawings and complete with lamp
fitting and accessories of Engineer or approved make.
A | 1200mm flourescent tube lighting |  | No. | 2
Switches
B | 5 Amps 2 gang one way switch |  | No | 1
Socket outlets
Supply and installation of fused shuttered switched socket outlet
to comply with relevant BS standard (Clipsal, Orange, Crabtree/
Tenby/ABB or equivalent). Wiring (including supply of earth wire
and all other material required) of above socket outlet using approved
type 2.5mm² PVC/PVC copper cable and 2.5mm² earth wire drawn
through securely fixed concealed PVC conduit in a ring circuit.
Socket outlet points
D | 13 A twin sockets outlet |  | No | 1
Cables, Cable pathways and Conduits
Supply, install, test and commission 450/750 volts 6491X cables with
all required accessories for proper installation and operation including
conduits, pipes( each cable in separate conduit or pipe), cable lugs,
ties... etc. as shown on drawing, as per the preamble, the specifications
and supervision engineer's requirements.
E | Supply, install and connect complete 1.5 sq. mm colour-coded SC
cables to lighting points drawn in Concealed /surface 20mm HG PVC
conduits, complete with draw boxes, switch boxes and other necessary
| accessories. |  | M | 10
F | Supply and install two compartment floor recessed metallic electrical
floor box with flap cover complete with lifting handle, cable cable flaps,
| as Crabtree Britmac or equal and approved |  | No. | 1
| CARRIED TO COLLECTION AT END OF ELEMENT 7 |  | US$
MAIN SUMMARY
| Ref. | TITLE |  | PAGE |  | AMOUNT
| 1 | ELEMENT NO. 1: SITE PREPARATION |  | 2/1
| 2 | ELEMENT NO. 2: SUBSTRUCTURES (PROVISIONAL) |  | 2/2
| 3 | ELEMENT NO. 3: WALLING |  | 2/3
| 4 | ELEMENT NO. 4: ROOF CONSTRUCTION AND FINISHES |  | 2/4
| 5 | ELEMENT NO. 5: FINISHES |  | 2/5
| 6 | ELEMENT NO. 6: DOORS |  | 2/6
| 7 | ELEMENT NO. 7: ELECTRICAL INSTALLATION AND SERVICES |  | 2/7
Grand Total
| TOTAL CARRIED TO GRAND SUMMARY |  | US$ |  |  | #VALUE!

## Comunal water point
ITEM NO. | DESCRIPTION | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
5- COMMUNAL WATER POINT
Yard
Excavation
Excavation including maintaining and supporting sides and keeping free from water, mud and fallen materials by bailing, pumping or otherwise
A | Prepare site by stripping top 200 mm of soil to remove all debris including sand (if any) from site and carting away spoil | m2 | 3.61
B | Excavate to reduce levels not exceeding 1.50m deep average depth 300mm | m2 | 3.61
Filing
C | 300 mm thick approved hardcore filling spread, well rammed and compacted in 150mm layers to receive concrete surface bed | m3 | 8.748
Insitu concrete: class 15: mix 1:3:6
D | 50mm blinding layer on hardcore surfaces | m2 | 3.61
E | Treat hardcore surface with approved insecticide | m2 | 3.61
Concrete work
Reinforced Concrete class 25
F | 75mm thick floor slab with surface steel troweled smooth | m3 | 2.451
G | 200mm thick floor slab with surface steel troweled smooth | m3 | 7.16
H | 200mm walls | m3 | 0.256
Reinforcement
I | Reinforcement bars (all sizes) as shown on drawings | kg | 197
Subtotal 1 Yard Collection
Sawn formwork
A | Formwork to edges of floor slab girth not exceeding 75mm, formwork to sides of walls and 100 x 100mm open drain channel | LS | 1
Finishes
Floor Finishes
Cement and sand mortar (1:3) in:
B | 30mm thick steel troweled screed | m2 | 3.61
Gate valve chamber
Excavation
Excavation including maintaining and supporting sides and keeping free from water, mud and fallen materials by bailing, pumping or otherwise
C | Pit excavation commencing at reduced levels depth not exceeding 1.50m deep | m3 | 0.288
D | Remove surplus excavated material from site | m3 | 0.144
E | Backfill around foundation | m3 | 0.144
Subtotal 2 to Yard Collection
Walling
A | 200mm Holow block walling | m2 | 34.8
Finishes
Cement and sand mortar (1:3) rendering in:
B | 15mm Both internal and external plaster to walls | m2 | 22.8
C | 12mm plaster to cover slab | m2 | 3.36
Water Supply System
Galvanized Mild Steel pipes class "B" medium thickness with and including jointing, fittings and fixe as described
D | 25 mm diameter inlet pipe | m | 9
E | 25 mm diameter brass gate valve with wheel and head | No | 7
| Subtotal 3 to Yard Collection |  |  |  | 0
YARD COLLECTION
Subtotal 1
Subtotal 2
Subtotal 3
YARD SUB TOTAL TO SUMMARY

## Animal troughs
ITEM NO. | DESCRIPTION |  |  | UNIT | QUANTITY | RATE (US$) | AMOUNT (US$)
6- CATTLE AND SHEEP WATER TROUGH
ELEMENT NO. 1: SITE PREPARATION
A | Clear site of all trees, bushes and shrubs, grab up roots and
| burn the arisings. |  |  | m2 | 16
B | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  |  | LS | 1
| CARRIED TO COLLECTION AT END OF ELEMENT 1 |  |  | US$
ELEMENT NO. 2: SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
A | Topsoil excavation average 200mm deep |  |  | m3 | 3.2
B | Excavate trench for foundation not exceeding 1.50 meters
| deep, starting from stripped levels |  |  | m3 | 12
Disposal
C | Return, fill and ram selected excavated material around
| foundations |  |  | m3 | 8
D | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  |  | m3 | 4
Hardcore or other approved filling, as described
E | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed |  |  | m3 | 2.4
Anti-termite treatment
F | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of hard-core |  |  | m2 | 2.4
Damp-proof membrane
G | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) |  |  | m2 | 2.4
Plain concrete class 15 in:
H | 50mm blinding under strip footing |  |  | m2 | 12
concrete class (20) as described, in:-
I | Ground beam |  |  | m3 | 2.448
J | 200mm thick surface bed laid in bays including all
| necessary formwork |  |  | m3 | 4
Reinforcement, as described:-[PROVISIONAL]
High yield square twisted reinforcement bars to B.S 4461
A | GROUND BEAM
| 10mm bars |  |  | Kg | 50.3472
| 8mm bars |  |  | Kg | 22.5624
Mesh fabric reinforcement to B.S 4483 and setting in
concrete with 300mm side and end laps
(measured nett-allow for laps).
B | Fabric ref. A142 weighing 2.22kg/ sq.metre, in surface
| bed |  |  | m2 | 2.4
Sawn formwork as described to:-
C | To edge of slab |  |  | m2 | 4.08
| CARRIED TO COLLECTION AT END OF ELEMENT 2 |  |  | US$
ELEMENT NO. 3: WALLING
SUPERSTRUCTURE WALLING
200x400mm Solid block walling bedded and jointed in
cement and sand (1:4) mortar, reinforcement with and
including 25mm wide x 20 gauge hoop iron at every
alternate course as described in:
B | 200mm thick walling Super-structure walling |  |  | m2 | 3.84
Damp-proof courses, as described, to walls
C | 200mm wide |  |  | m | 26.2
| CARRIED TO COLLECTION AT END OF ELEMENT 3 |  |  | US$
ELEMENT NO. 4: FINISHES
15 mm cement and sand (1:3) render, finished with
woodfloat to:-
A | Concrete or masonry surfaces internally and externally |  |  | m2 | 3.84
12mm (minimum) two coat lime plaster as described to
B | Concrete or masonry surfaces internally |  |  | m2 | 3.84
Floor Finishes
Cement and sand (1:3) screeds, backings, beds etc
C | 40mm bed finished floor screed |  |  | m2 | 2.4
Painting and decorating
Prepare and apply three coats first quality emulsion
paint on:-
D | Plastered walls externally |  |  | m2 | 3.84
Prepare and apply three coats first quality silk vinyl
emulsion paint on:-
E | Plastered surfaces internally |  |  | m2 | 3.84
| CARRIED TO COLLECTION AT END OF ELEMENT 5 |  |  | US$
ELEMENT NO. 5: PLUMBING
PIPE AND FITTINGS
All pipework shall be of HDPE or polypropylene random
PP-R pipes to DIN8077 and DIN8078 all pipes and fittings
to conform to PN20
| A | Supply 250mm dia. Straight pipe laid and jointed in |  | m | 20
trench not exceeding 500mm
VALVES (INCLUDING CHAMBERS FITTINGS ETC)
250mm flanges double acting air relief valve PN20 capable
| B | of giving an inflow of 39m³/mm at a pressure of 0.2 bar |  | No | 2
WASHOUTS
| C | 5mm DN washout on 150mm DN steel pipe
|  | complete with 75mm NP16 Sluice Valve, extension |  | No | 2
pipe and Headwall to the nearest natural drain
TEES
| D | 150mm dia flanged Tee for washouts and branches |  | NO | 2
| E | 250 mm dia. Tee |  | NO | 2
ARRIED TO COLLECTION AT END OF ELEMENT 5
MAIN SUMMARY
| Ref. |  | TITLE |  |  |  | AMOUNT
| 1 |  | ELEMENT NO. 1: SITE PREPARATION
| 2 |  | ELEMENT NO. 2: SUBSTRUCTURES (PROVISIONAL)
| 3 |  | ELEMENT NO. 3: WALLING
| 4 |  | ELEMENT NO. 4: FINISHES
| 5 |  | ELEMENT NO. 5: PLUMBING
| TOTAL CARRIED TO GRAND SUMMARY | [5 empty] | #VALUE!

## Fence
ITEM | DESCRIPTION |  | UNIT | QNTY | RATE US$ | AMT US$
7- FENCE AND GATE
ELEMENT No. 1: GATE
The contractor will provide all material and construct a steel
gate maesuring approximately 4500x2100m.
Given the location and site conditions, the contractor is
advised to make a physical assesment of the site before
tendering.
A | Excavate for column pads, depth not exceeding
1.5m and of 1.5 x 1.5 mm width commencing at the original
| ground level, and cart away to spoil as directed |  | m3 | 6.75
Reinforced Concrete using 3/4 + 1/2" mix machine
crushed Ballast in:
B | Vibrated reinforced concrete (class 25) column base, 350mm deep |  | m3 | 0.7875
C | Ditto in columns 600x600mm thick, average height of 2.7 m
| with 1.5 m being the foundation column |  | m3 | 1.944
D | Assorted high tensile twisted steel reinforcement bars to B.S 4446. |  | Kg | 200
E | Sawn formwork to vertical sides of the columns |  | m2 | 10
F | 15mm thick cement/Sand plaster to vertical sides of the columns |  | m2 | 10
G | 350x350x25mm thick P.C.C coping stone |  | No | 2
Main and pedestrian gates
H | Supply and fix double leaf steel gate size 4500x 2100mm high
with small pedestrian door made from 3mm thick steel plate
welded on both sides of the freme. Frame as follows: 75x50x3mm
thick RHS external members and 25mm SHS 3mm thick secondary
members, fixed onto the concrete columns using heavy duty steel
pin hinges; with all fastening accessories including all cutting
welding, grinding and priming with one coat of grey oxide before
fixing. The gate should also have peep holes of not more that
25mm dia with a slilding door. It should also have 2 locking
| mechanisms, top and bottom. |  | NO | 2
| Sub-Total for main and pestrian gate |  |  |  |  | #VALUE!
ELEMENT No. 2 : FENCE
The contractor is reminded to include in his pricing,
the cost of supply, cutting, waste and erection and all other
necessary fittings including welding lugs or fishtailing onto
the 50x50x6mm angle bars. Angle bars and the necessary
fixing and anchorage to be treated as described in the
specifications.
Fence construction should be according to BS 1722-Part 10
A | Clear the perimeter of the fencing area of all bushes scrubs and obstructions |  | m2 | 60
B | Excavate 300x300x500 deep holes to receive mass concrete (1:3:6) bases as shown in the drawings.
|  |  | m3 | 1.5
C | Supply 50x5mm CHS welded to form Y-shaped posts with ends closed as
shown in the drawings, bottom end fixed with 100x100mmx3mm plate
and bedded in mass concrete.The post to be 2500mm high from ground
| level to the Y-joint. Allow for drlling 7No holes as shown. |  | NO | 33
D | Extra Over 50x5mm posts for bracing on either side every fourth
| intermediate post and all corner posts. |  | NO | 33
Mass Concrete Mix 1:3:6/20mm using 3/4 Local Ballast in:
E | Supply all materials and cast 0.3m diameter x 0.6m depth mass concrete
class Q (1:3:6) to concrete the 50mm dia. CHS poles while ensuring they
remain plumb 600mm deep below the ground level and 2500mm (2.5m)
| above ground level. |  | m3 | 1.5
F | Supply and weld a 12mm high tensile steel rod along the bases of the posts
for anchoring the chainlink to the ground along the whole length of the fence.
| Allow for excavating 200mm deep along the fence to fix the rod. |  | m | 100
G | Allow for curing of all concrete works |  | Item | 1
H | Supply and fix 3No strands of 12G barbed wire bound onto either sides
| of the Y post using 3mm galvanised wire as shown in the drawings. |  | m | 100
I | Ditto for posts |  | m | 14.29
J | Supply and and fix 2500mm high HEAVY GUAGE 12 chainlink to posts using 3mm
galvanised wire. Allow for securing the chainlink to a 12mm reinforcement
| bar welded at the base btween the posts. |  | m | 100
K | Supply and fix razer wire secured on the chainlink, barbed wire and Y posts
| by binding wire and rolled approximately 600mm dia. |  | m | 100
L | Prepare and apply one under coat of epoxy based primer and two finishing
| epoxy based paints to metal surfaces n.e 250mm in alternate bands of 300mm |  | No. | 66
Total carried to summary
ELEMENT NO. 3 : MAIN SUMMARY
| ELEMENT No. | TITLE |  | PAGE |  | AMOUNT
| 1 | ELEMENT No. 1: GATE |  | 1/2
| 2 | ELEMENT No. 2 : FENCE |  | 2/2
Total
Total carried to grand summary