## BOQ of Solar System for Balcad
PV-off-grid solar system for Balcad School
ITEM | DESCRIPTION | UNIT | QTY | Unit price | Price
Note:- Proposed Installation of solar energy system for Balcad (2.7 kW PV and 19.2kWh storrage 60% discharge)
1 | Solar Module- 345W Monocrystalline or Equivallent Monocrystalline Half-cell - A grade - Full Black- 25 years warranty -Module efficiency: 20.4% -Voltage at Pmax: 35.3V -Current at Pmax: 9.78A -Open-Circuit Voltage: 41.3V -Short Circuit Current: 10.37A -Max. System Voltage: 1500V DC | UNIT | 8 |  | 0
2 | Battery: Deep cycle carbon 12V/200ah -Maximum charging current: 80A -Maximum discharge current: 2000A(5 sec) -Fully ceritified | Unit | 8 |  | 0
3 | Off-grid inverter- 3000watt High quality pure sinewave (Victron or simmilar quality inverter) -Rated Surge power: 9kVa (20ms) -Multiple functions, LCD screen, low noise -48v battery input, 220v single phase output -AC charging function | Unit | 1 |  | 0
4 | MPPT charge controller: High quality heat sink charger Rated Current : 100A Rated Voltage :48V/AUTO Maximum Battery Voltage : 48V Maximum PV Voltage : 150V | Unit | 1 |  | 0
5 | PV Mounting structure for PV modules Original aluminium mounting structure for mounting the PV-modules. For roof top. | LSM | 1 |  | 0
6 | CABLES AND ACCESSORIES - PV cables 6mm (60m) - Water proof MC4 singel and parallel connectors (6xparallel - 2xsingel) - AC cables 16mm for the inverter and charger (40m) - AC cables 35mm for battery (20m) - Complete set AC electrical panel with MCB's, RCCB - Complete earthing equipment - Battery rack | Set | 1 |  | 0
7 | Service 1 - Installation of solar system - Testing and Commissioning - Training | Lumps | 1 |  | 0
8 | Service 2 - Transport to Balcad | Lumps | 1 |  | 0
| Total |  |  |  | 0